## Sheet1
Description | IEEE 1547.1 | IEC 61850-7-420 | IEEE 1815.2 | IEEE 2030.5 | SunSpec Modbus
Nameplate | Active Power (unity) | DGEN.WMaxRtg | AI4 | DERCapability::rtgMaxW | 702.WMaxRtg
Nameplate | Active Power (over-excited) | DGEN.WGnOvPFRtg | AI6-AI7 | DERCapability::rtgOverExcitedW | 702.WOvrExtRtg
Nameplate | Power Factor (over-excited) | DGEN.OvPFRtg | AI8 | DERCapability::rtgOverExcitedPF | 702.WOvrExtRtgPF
Nameplate | Active Power (under-excited) | DGEN.WGnUnPFRtg | AI9-AI10 | DERCapability::rtgUnderExcitedW | 702.WUndExtRtg
Nameplate | Power Factor (under-excited) | DGEN.UnPFRtg | AI11 | DERCapability::rtgUnderExcitedPF | 702.WUndExtRtgPF
Nameplate | Apparent Power (Max) | DGEN.VAMaxRtg | AI15 | DERCapability::rtgMaxVA | 702.VAMaxRtg
Nameplate | Normal (operating category) | DGEN.Ieee1547Cat1 | AI22 | DERCapability::rtgNormalCategory | 702.NorOpCatRtg
Nameplate | Abnormal (operating category) | DGEN.Ieee1547Cat2 | AI23 | DERCapability::rtgAbnormalCategory | 702.AbnOpCatRtg
Nameplate | Reactive Power (Max Injected) | DGEN.VarMaxSupRtg | AI12 | DERCapability::rtgMaxVar | 702.VarMaxInjRtg
Nameplate | Reactive Power (Max Absorbed) | DGEN.VarMaxAbgRtg | AI13 | DERCapability::rtgMaxVarNeg | 702.VarMaxIAbsRtg
Nameplate | Active Power (Max Charge) | DSTO.WChaUnPFRtg | AI15 | DERCapability::rtgMaxChargeRateW | 702.WChaRteMaxRtg
Nameplate | Apparent Power (Max Charge) | DSTO.VAMaxChaRtg | AI16 | DERCapability::rtgMaxChargeRateVA | 702.WChaRteMaxRtg
Nameplate | Voltage AC (nominal) | DECP.VRef | AI29-AI30 | DERCapability::rtgVNom | 702.VNomRtg
Nameplate | Voltage AC (max) | DGEN.VMaxRtg | AI3 | DERCapability::rtgMaxV | 702.VMaxRtg
Nameplate | Voltage AC (min) | DGEN.VMinRtg | AI2 | DERCapability::rtgMinV | 702.VMinRtg
Nameplate | Supported Control Mode Functions | DVRT, DFRT, DFWP, DWLM, DVWC, DFWC, DVAR, DFPF, DVVC, DWVR | BI31-BI51 | DERCapability::modesSupported | 702.CtrlModes
Nameplate | Reactive Susceptance | DGEN.SuscRtg | AI21 | DERCapability::rtgReactiveSusceptance | 702.ReactSusceptRtg
Nameplate | Manufacturer | LPHD.PhyNam.vendor | N/A | DeviceInformation::mfID | 1.Mn
Nameplate | Model | LPHD.PhyNam.model | N/A | DeviceInformation::mfModel | 1.Md
Nameplate | Serial Number | LPHD.PhyNam.serNum | N/A | DeviceInformation::mfSerNum | 1.SN
Nameplate | Version | LPHD.PhyNam.swRev | N/A | DeviceInformation::mfHwVer, DeviceInformation::swVer | 1.Vr
Nameplate | Storage Capacity | DSTO.WhRtg | AI16
Configuration | Active Power (unity) | DGEN.WMax |  |  | 702.Wmax
Configuration | Active Power (over-excited) | DGEN.WGnOvPFRtg |  |  | 702.WMaxOvrExt
Configuration | Power Factor (over-excited) | DGEN.OvPFRtg |  |  | 702.WOvrExtPF
Configuration | Active Power (under-excited) | DGEN.WGnUnPFRtg |  |  | 702.WMaxUndExt
Configuration | Power Factor (under-excited) | DGEN.UnPFRtg |  |  | 702.WUndExtPF
Configuration | Apparent Power (Max) | DGEN.VAMax |  |  | 702.VAMax
Configuration | Normal (operating category) | DGEN.RegCap |  |  | 702.IntIslandCat
Configuration | Abnormal (operating category) | DGEN.RegCap
Configuration | Reactive Power (Max Injected) | DGEN.VarMaxSupRtg |  |  | 702.VarMaxInjRtg
Configuration | Reactive Power (Max Absorbed) | DGEN.VarMaxAbgRtg |  |  | 702.VarMaxAbsRtg
Configuration | Active Power (Max Charge) | DSTO.WChaUnPFRtg |  |  | 702.WChaRteMax
Configuration | Apparent Power (Max Charge) | DSTO.VAMaxChaRtg |  |  | 702.VAChaRteMax
Configuration | Voltage AC (nominal) | DECP.VRef |  |  | 702.Vnom
Configuration | Voltage AC (max) | DGEN.Vmax
Configuration | Voltage AC (min) | DGEN.Vmin
Configuration | Supported Control Mode Functions | DVRT, DFRT, DFWP, DWLM, DVWC, DFWC, DVAR, DFPF, DVVC, DWVR
Configuration | Reactive Susceptance | DGEN.SuscRtg
Configuration | Manufacturer | LPHD.PhyNam.vendor
Configuration | Model | LPHD.PhyNam.model
Configuration | Serial Number | LPHD.PhyNam.serNum
Configuration | Version | LPHD.PhyNam.swRev
Configuration | Storage Capacity | DSTO.WhRtg
Monitoring | Active Power | DECP.MMXU.TotW | AI537 | ReadingType::accumulationBehaviour = 12 ReadingType::commodity = 1 ReadingType::flowDirection = 19 ReadingType::kind = 37 ReadingType::uom = 38 | 701.W
Monitoring | Reactive Power | DECP.MMXU.TotVAr | AI541 | ReadingType::accumulationBehaviour = 12 ReadingType::commodity = 1 ReadingType::flowDirection = 19 ReadingType::kind = 37 ReadingType::uom = 63 | 701.Var
Monitoring | Voltage(s) | DECP.MMXU.PhV.phsA.mag, DECP.MMXU.PhV.phsB.mag, DECP.MMXU.PhV.phsC.mag | AI547-AI553 | ReadingType::accumulationBehaviour = 12 ReadingType::commodity = 1 ReadingType::flowDirection = 1 ReadingType::phase = {phase} ReadingType::uom = 29 | 701.LLV, 701.LNV, 701.VL1L2, 701.VL1, 701.VL2L3, 701.VL2, 701.VL3L1, 701.VL3
Monitoring | Frequency | DECP.MMXU.Hz | AI554-AI556 | ReadingType::accumulationBehaviour = 12 ReadingType::commodity = 1 ReadingType::flowDirection = 1 ReadingType::uom = 33 | 701.Hz
Monitoring | Operation State | DGEN.DERState | AI536 | DERStatus::operationalModeStatus | 701.St
Monitoring | Connection Status | DSTO.DERState.1 | BI10-BI24 | DERStatus::genConnectStatus DERStatus::storConnectStatus | 701.ConnSt
Monitoring | Alarm Status | CALH.GrAlm | BI0-BI9 | DERStatus::alarmStatus | 701.Alrm
Monitoring | Operation SoC | DSTO.SocUsePct | AI48 | DERStatus::stateOfChargeStatus | 713.SoC
Constant PF | Enable | DFPF.ModEna | BO28:BI80 |  | 704.PFWInjEna
Constant PF | Injection/Absorption setting | DFPF.PFGnTgt, DFPF.PFLodTgt | AO210-AO211:AI288-AI289 | DERControl::opModFixedPFInjectW | 704.PFWInj.PF
Constant PF | Excitation setting | DFPF.PFExtSet | BO10-BO11:BI29-BI30 | DERControl::opModFixedPFInjectW.excitation | 704.PFWInj.Ext
Volt-VAR | Enable | DVVR.ModEna | BO29:BI81 |  | 705.Ena
Volt-VAR | Vref | DECP.VRef | AO0-AO1:AI29-AI30 | DERCurve::vRef | 705.VRef
Volt-VAR | Autonomous Vref Adjustment enable | DVVR.VRefAdjEna | BO41:BI93 | DERCurve::autonomousVRefEnable | 705.VRefAutoEna
Volt-VAR | Vref Adjustment Time Constant | DVVR.VRefTmms | AO220:AI300 | DERCurve::autonomousVRefTimeConstant | 705.VRefAutoTms
Volt-VAR | V/Q Curve Points | DVVR.VVArCrv | AO217,AO244-AO448:AI303 | DERControl::opModVoltVar::CurveData | 705.Crv.Pt[#].V, 705.Crv.Pt[#].Var
Volt-VAR | Open Loop Response Time | DVVR.OpnLoopMax | AO218-AO219:AI298-AI299 | DERControl::opModVoltVar::openLoopTms | 705.RspTms
Watt-VAR | Enable | DWVR.ModEna | BO30:BI82 |  | 712.Ena
Watt-VAR | P/Q Curve Points | DWVR.WVArCrv | AO226,AO244-AO448:AI308, AI328-AI532 | DERControl::opModWattVar::CurveData | 712.Crv.Pt[#].W, 712.Crv.Pt[#].Var
Constant VAR | Enable | DVAR.ModEna | BO27:BI79 |  | 704.VarSetEna
Constant VAR | VAR Setting | DVAR.VArTgt | AO203:AI281 | DERControl::opModFixedVar DERControl::opModTargetVar | 704.VarSetPct
Volt-Watt | Enable | DVWC.ModEna | BO25:BI77 |  | 706.Ena
Volt-Watt | V/P Curve Points | DVWC.VWCrv | AO173,AO244-AO448:AI248,AI328-AI532 | DERControl::opModVoltWatt::CurveData | 706.Crv.Pt[#].V, 706.Crv.Pt[#].W
Volt-Watt | Open Loop Response Time | DVWC.OpnLoopMax | AO175-AO176:AI251-AI252 | DERControl::opModVoltWatt::openLoopTms | 706.RspTms
Voltage Trip | HV Trip Curve Points | DHVT.TrZnSt, PTOV.TmVCrv | AO23,AO244-AO448:AI73,AI328-AI532 | DERControl::opModHVRTMustTrip::CurveData | 707.MustTrip.Crv.Pt[#].V, 707.MustTrip.Crv.Pt[#].Tms
Voltage Trip | LV Trip Curve Points | DLVT.TrZnSt, PTUV.TmVCrv | AO24,AO244-AO448:AI74,AI328-AI532 | DERControl::opModLVRTMustTrip::CurveData | 708.MustTrip.Crv.Pt[#].V, 708.MustTrip.Crv.Pt[#].Tms
Momentary Cessation | HV Trip Curve Points | DHVT.CeaZnSt, PTOV.TmVCrv | AO25,AO244-AO448:AI75,AI328-AI532 | DERControl::opModHVRTMomentaryCessation::CurveData | 707.MomCess.Crv.Pt[#].V, 707.MomCess.Crv.Pt[#].Tms
Momentary Cessation | LV Trip Curve Points | DLVT.CeaZnSt, PTUV.TmVCrv | AO26,AO244-AO448:AI76,AI328-AI532 | DERControl::opModLVRTMomentaryCessation::CurveData | 708.MomCess.Crv.Pt[#].V, 708.MomCess.Crv.Pt[#].Tms
Frequency Trip | HV Trip Curve Points | DHFT.TrZnSt, PTOF.StrVal | AO28,AO244-AO448:AI79,AI328-AI532 | DERControl::opModHFRTMustTrip::CurveData | 709.MustTrip.Crv.Pt[#].Hz, 707.MustTrip.Crv.Pt[#].Tms
Frequency Trip | LV Trip Curve Points | DLFT.TrZnSt, PTUF.StrVal | AO29,AO244-AO448:AI80,AI328-AI532 | DERControl::opModLFRTMustTrip::CurveData | 710.MustTrip.Crv.Pt[#].Hz, 710.MustTrip.Crv.Pt[#].Tms
Frequency-Watt | dbof | DHFW.HzStr | AO62-AO63:AI121-AI122 | DERControl::opModFreqDroop::dBOF | 711.Ctl.DbOf
Frequency-Watt | dbuf | DLFW.HzStr | AO66-AO67:AI125-AI126 | DERControl::opModFreqDroop::dBUF | 711.Ctl.DbUf
Frequency-Watt | kof | DHFW.WGra | AO64-AO65:AI123-AI124 | DERControl::opModFreqDroop::kOF | 711.Ctl.KOf
Frequency-Watt | kuf | DLFW.WGra | AO68-AO69:AI127-AI128 | DERControl::opModFreqDroop::kUF | 711.Ctl.Kuf
Frequency-Watt | Open Loop Response Time | DHFW.OpnLoopMax, DLFW.OpnLoopMax | AO72-AO73:AI131-AI132 | DERControl::opModFreqDroop::openLoopTms | 711.Ctl.RspTms
Enter Service | Permit service | DCTE.RtnSrvAuto, DCTE.RtnSrvAuth | BO3:BI16 | DERControl::opModEnergize | 703.ES
Enter Service | ES Voltage High | DCTE.VHiLim | AO6:AI50 | DERSettings::setESHighVolt DefaultDERControl::setESHighVolt | 703.ESVHi
Enter Service | ES Voltage Low | DCTE.VLoLim | AO7:AI51 | DERSettings::setESLowVolt DefaultDERControl::setESLowVolt | 703.ESVLo
Enter Service | ES Frequency High | DCTE.HzHiLim | AO8:AI52 | DERSettings::setESHighFreq DefaultDERControl::setESHighFreq | 703.ESHzHi
Enter Service | ES Frequency Low | DCTE.HzLoLim | AO9AI53 | DERSettings::setESLowFreq DefaultDERControl::setESLowFreq | 703.ESHzLo
Enter Service | ES Delay | DCTE.RtnSrvDlyTim | AO10:AI54 | DERSettings::setESDelay DefaultDERControl::setESDelay | 703.ESDlyTms
Enter Service | ES Randomized Delay | DCTE.RtnSrvDlyTim | AO11:AI55 | DERSettings::setESRandomDelay DefaultDERControl::setESRandomDelay | 703.ESRndTms
Enter Service | ES Ramp Time | DCTE.RtnSrvRmpTim | AO12:AI56 | DERSettings::setESRampTms DefaultDERControl::setESRampTms | 703.ESRmpTms
Limit Watt | Enable | DWMX.ModEna, DWMN.ModEna | BO17:BI69 |  | 704.WMaxLimPctEna
Limit Watt | Watt Setting | DWMX.LimW, DWMN.LimW | AO87-AO88:AI48-AI140 | DERControl::opModMaxLimW | 704.WMaxLimPct

## Sheet2
Description | IEEE 1547.1 | IEC 61850-7-420 | Explanation
Monitoring | Alarm Status | CALH.GrAlm | System Has Priority 1 Alarms
Enter Service | ES Frequency High | DCTE.HzHiLim | The frequency high limit of the normal frequency range. The measured frequency must be below this high limit before the DER may be allowed to return to service.
Enter Service | ES Frequency Low | DCTE.HzLoLim | The frequency low limit of the normal frequency range. The measured frequency must be above this low limit before the DER may be allowed to return to service.
Enter Service | Permit service | DCTE.RtnSrvAuth | Authorization setting that permits the DER to return to service. True = authorized; False = not authorized. If true, the DER may or may not initiate the return to service process, depending on other factors. The CeaEngz command sets this setting to False.
Enter Service | Permit service | DCTE.RtnSrvAuto | If true, the DER is authorized to automatically return to service; if false, the DER must wait until an external RtnSvcAuth is received to allow it to return to service.
Enter Service | ES Delay | DCTE.RtnSrvDlyTim new RtnDITmms | Time delay (ms) before returning to service in order to ensure that both the frequency and voltage are within their high and low limits
Enter Service | ES Randomized Delay | DCTE.RtnSrvDlyTim new RtnDITmms | Time delay (ms) before returning to service in order to ensure that both the frequency and voltage are within their high and low limits
Enter Service | ES Ramp Time | DCTE.RtnSrvRmpTim new RtnRmpTmms | Return to service duration (ms) that is a time for ramping up that must not be exceeded. Active power shall increase linearly, or in a stepwise linear ramp, with an average rate-of-change not exceeding the DER nameplate active power rating divided by this return to service duration.
Enter Service | ES Voltage High | DCTE.VHiLim | The voltage high limit of the normal voltage range. The measured voltage must be below this high limit before the DER may be allowed to return to service.
Enter Service | ES Voltage Low | DCTE.VLoLim | The voltage low limit of the normal voltage range. The measured voltage must be above this low limit before the DER may be allowed to return to service.
Monitoring | Frequency | DECP.MMXU.Hz | (inherited from: MMXU) Frequency [Hz].
Monitoring | Voltage(s) | DECP.MMXU.PhV.phsA.mag | (inherited from: MMXU) Phase to ground (line) voltages.
Monitoring | Voltage(s) | DECP.MMXU.PhV.phsB.mag | (inherited from: MMXU) Phase to ground (line) voltages.
Monitoring | Voltage(s) | DECP.MMXU.PhV.phsC.mag | (inherited from: MMXU) Phase to ground (line) voltages.
Monitoring | Reactive Power | DECP.MMXU.TotVAr | (inherited from: MMXU) Total reactive power in a three-phase circuit [Var].
Monitoring | Active Power | DECP.MMXU.TotW | (inherited from: MMXU) Total real power in a three-phase circuit [W].
Nameplate | Voltage AC (nominal) | DECP.VRef | (inherited from: PhysicalElectricalConnectionPointLN) Default reference voltage for functions using voltage at this ECP as input. It may be overridden by V
Volt-VAR | Vref | DECP.VRef | (inherited from: PhysicalElectricalConnectionPointLN) Default reference voltage for functions using voltage at this ECP as input. It may be overridden by VRef setpoints in specific operational functions.
Volt-VAR | Autonomous Vref Adjustment enable | DVVR.VRefAdjEna | Default reference offset voltage setting for functions using voltage as input at this ECP if there should be an offset from the VRef value.
Nameplate | Supported Control Mode Functions | DFPF | LN DFPF: Set Fixed Power Factor operational function
Constant PF | Enable | DFPF.ModEna new ReqPF | If the quality attribute for this power factor value is set to "invalid", then the value of this requested DO is not valid and should not be used by other functions. Therefore, if this function is not enabled or has some other constraining factor, the quality attribute must be set to "invalid".
Constant PF | Excitation setting | DFPF.PFExtSet new PFLodExtQu d | PF excitation setpoint when charging / load to indicate which quadrant to go to when switching from load to discharging: 0 = Injecting reactive power – Q2, 1 = Absorbing reactive power – Q3. Its stVal attribute reflects the value of the setpoint that is requested.
Constant PF | Injection/Absorption setting | DFPF.PFGnTgt new PFGnTgtSpt | Target power factor setpoint when generating. PFSign (in MMXU) defines what convention is in use. The power factor target is a number between -1 and 1, and is used in conjunction with PFGnExtSet to indicate whether it to set it over or under excited. Its mxVal attribute reflects the value of the setpoint that is requested.
Constant PF | Injection/Absorption setting | DFPF.PFLodTgt new PFLodTgtSpt | Target power factor setpoint when acting as a load (consuming, charging). PFSign (in MMXU) defines what convention is in use. The power factor target is a number between -1 and 1, and is used in conjunction with PFLodExtSet to indicate whether it to make it over or under excited. Its mxVal attribute reflects the value of the setpoint that is requested.
Nameplate | Supported Control Mode Functions | DFRT | LN DHFT and DLFT: Frequency Ride-Through
Nameplate | Supported Control Mode Functions | DFWC | LN DHFW: High Frequency-Active Power operational function and LN DLFW: Low Frequency-Active Power operational function
Nameplate | Supported Control Mode Functions | DFWP | Active power operational functions (there are a few in this category which need a deeper dive): DVWC DWGC DWFL DAGC DTCD DWMX DWMN
Monitoring | Operation State | DGEN.DERState | (inherited from: DER_StateAbstractLN) Current state of operation of the distributed energy resource.
Nameplate | Normal (operating category) | DGEN.Ieee1547Cat1 | IEEE 1547-2018 B.3 Normal and abnormal performance category standard approach
Nameplate | Abnormal (operating category) | DGEN.Ieee1547Cat2 | IEEE 1547-2018 B.3 Normal and abnormal performance category standard approach
Nameplate | Power Factor (over-excited) | DGEN.OvPFRtg | (inherited from: DER_NameplateRatingsLN) Specified Over-Excited Power Factor Rating
Nameplate | Reactive Susceptance | DGEN.SuscRtg | Susceptance rating in siemens
Nameplate | Power Factor (under-excited) | DGEN.UnPFRtg | (inherited from: DER_NameplateRatingsLN) Specified Under-Excited Power Factor
Nameplate | Apparent Power (Max) | DGEN.VAMaxRtg | (inherited from: GeneratorNameplateRatingsLN) Nameplate maximum apparent power generation rating
Nameplate | Reactive Power (Max Injected) | DGEN.VarMaxAbgRtg new DGEN.AvarMaxRtg | Rating for maximum absorbing reactive power
Nameplate | Reactive Power (Max Absorbed) | DGEN.VarMaxSupRtg new DGEN.IvarMaxRtg | Rating for maximum supply (injection) reactive power
Nameplate | Voltage AC (max) | DGEN.VMaxRtg | (inherited from: GeneratorNameplateRatingsLN) Maximum voltage rating
Nameplate | Voltage AC (min) | DGEN.VMinRtg | (inherited from: GeneratorNameplateRatingsLN) Minimum voltage rating
Nameplate | Active Power (over-excited) | DGEN.WGnOvPFRtg | Nameplate active power generation rating at specified over-excited power factor, OvPFRtg
Nameplate | Active Power (under-excited) | DGEN.WGnUnPFRtg | Nameplate active power generation rating at specified under-excited power factor, UnPFRtg
Nameplate | Active Power (unity) | DGEN.WMaxRtg | Nameplate maximum active generation power rating at unity power factor
Frequency Trip | HV Trip Curve Points | DHFT.TrZnSt | (inherited from: RideThroughLN) True = the voltage or frequency of the Referenced ECP exceeds the Trip zone, False = the voltage or frequency does not exceed the Trip zone.
Frequency-Watt | dbof | DHFW.HzStr | The frequency which must be higher (lower) than the reference frequency at which to start reducing (increasing) power output.
Frequency-Watt | Open Loop Response Time | DHFW.OpnLoopMax new OplTmsMax | (inherited from: LowPassFilterOnFunctionOutputLN) Maximum (Fast-as-possible) open loop response time in seconds. The DER should reach OplPct (e.g. 90 % or 95 %) of the delta between its current value and the requested value by the end of this time period. It may go as fast as it can, while still respecting any limiting ramp rates. Is equivalent to 3 tau in case of a first order low pass filter and the target percentage is equal to 95 %.
Frequency-Watt | kof | DHFW.WGra | (inherited from: FrequencyActivePowerLN) If curves are not used, this defines a single active decreasing (increasing) power gradient while generating or consuming in percent of WMax per Hz during a high (low) frequency condition
Momentary Cessation | HV Trip Curve Points | DHVT.CeaZnSt | (inherited from: RideThroughLN) True = the voltage or frequency of the Referenced ECP is within the Momentary Cessation zone; False = the voltage or frequency is not within the Momentary Cessation zone.
Voltage Trip | HV Trip Curve Points | DHVT.TrZnSt | (inherited from: RideThroughLN) True = the voltage or frequency of the Referenced ECP exceeds the Trip zone, False = the voltage or frequency does not exceed the Trip zone.
Frequency Trip | LV Trip Curve Points | DLFT.TrZnSt | (inherited from: RideThroughLN) True = the voltage or frequency of the Referenced ECP exceeds the Trip zone, False = the voltage or frequency does not exceed the Trip zone.
Frequency-Watt | dbuf | DLFW.HzStr | The frequency which must be higher (lower) than the reference frequency at which to start reducing (increasing) power output.
Frequency-Watt | Open Loop Response Time | DLFW.OpnLoopMax new OplTmsMax | (inherited from: LowPassFilterOnFunctionOutputLN) Maximum (Fast-as-possible) open loop response time in seconds. The DER should reach OplPct (e.g. 90 % or 95 %) of the delta between its current value and the requested value by the end of this time period. It may go as fast as it can, while still respecting any limiting ramp rates. Is equivalent to 3 tau in case of a first order low pass filter and the target percentage is equal to 95 %.
Frequency-Watt | kuf | DLFW.WGra | (inherited from: FrequencyActivePowerLN) If curves are not used, this defines a single active decreasing (increasing) power gradient while generating or consuming in percent of WMax per Hz during a high (low) frequency condition
Momentary Cessation | LV Trip Curve Points | DLVT.CeaZnSt | (inherited from: RideThroughLN) True = the voltage or frequency of the Referenced ECP is within the Momentary Cessation zone; False = the voltage or frequency is not within the Momentary Cessation zone.
Voltage Trip | LV Trip Curve Points | DLVT.TrZnSt | (inherited from: RideThroughLN) True = the voltage or frequency of the Referenced ECP exceeds the Trip zone, False = the voltage or frequency does not exceed the Trip zone.
Monitoring | Connection Status | DSTO.DERState.1 | (inherited from: DER_StateAbstractLN) Current state of operation of the distributed energy resource.
Monitoring | Operation SoC | DSTO.SocUsePct new DSTO.UseSocPct | (inherited from: DER_StorageLN) Usable state of charge (expressed as percent of total usable energy capacity UseWh) which may be directly measured or calculated
Nameplate | Apparent Power (Max Charge) | DSTO.VAMaxChaRtg new ChaVAMaxRtg | Nameplate maximum apparent charging power rating
Nameplate | Active Power (Max Charge) | DSTO.WChaUnPFRtg new ChaWUnPFRtg | Active power charging rating at specified underexcited PF
Nameplate | Storage Capacity | DSTO.WhRtg | (inherited from: StorageNameplateRatingsLN) Nameplate energy storage capacity rating in Wh
Nameplate | Supported Control Mode Functions | DVAR | LN DVAR: Constant Reactive Power operational function
Constant VAR | Enable | DVAR.ModEna
Constant VAR | VAR Setting | DVAR.VArTgt new VArTgtSpt | (inherited from: ReactivePowerLN) Target reactive power setpoint as absolute value. Its mxVal attribute reflects the value of the setpoint that is requested.
Nameplate | Supported Control Mode Functions | DVRT | LN DHVT and DLVT: Voltage ride-through
Nameplate | Supported Control Mode Functions | DVVC maybe DVVR | LN DVVR: Voltage-Reactive Power (V-var) operational function
Volt-VAR | Enable | DVVR.ModEna
Volt-VAR | Open Loop Response Time | DVVR.OpnLoopMax new OplTmsMax | (inherited from: LowPassFilterOnFunctionOutputLN) Maximum (Fast-as-possible) open loop response time in seconds. The DER should reach OplPct (e.g. 90 % or 95 %) of the delta between its current value and the requested value by the end of this time period. It may go as fast as it can, while still respecting any limiting ramp rates. Is equivalent to 3 tau in case of a first order low pass filter and the target percentage is equal to 95 %.
Volt-VAR | Vref Adjustment Time Constant | DVVR.VRefTmms | Time (in ms) over which to sample voltage through a low pass filter to create an average voltage over that time
Volt-VAR | V/Q Curve Points | DVVR.VVArCrv | (DVVR) Paired array of independent and dependent variables For crvPts: xVal = Delta voltage from nominal (VRefSet minus percentages of nominal voltage) yVal = Percent of reactive power, either % of active power WMax, or % of reactive power VArMax or VArAvl, as set in ReactivePowerReferenceKind
Nameplate | Supported Control Mode Functions | DVWC | LN DVWC: Voltage-Active Power (V-W) operational function
Volt-Watt | Enable | DVWC.ModEna
Volt-Watt | Open Loop Response Time | DVWC.OpnLoopMax new OplTmsMax | (inherited from: LowPassFilterOnFunctionOutputLN) Maximum (Fast-as-possible) open loop response time in seconds. The DER should reach OplPct (e.g. 90 % or 95 %) of the delta between its current value and the requested value by the end of this time period. It may go as fast as it can, while still respecting any limiting ramp rates. Is equivalent to 3 tau in case of a first order low pass filter and the target percentage is equal to 95 %.
Volt-Watt | V/P Curve Points | DVWC.VWCrv | (DVWC) Paired array of independent and dependent variables For crvPts: xVal = voltage at the referenced ECP of this operational function yVal = active power or percent of WMax (ChaWMax), set by DepRef Maximum power curve delineating the limits for 4 zones – High voltage generating gradients – Low voltage generation gradients – High voltage consuming gradients – Low voltage consuming gradients
Nameplate | Supported Control Mode Functions | DWLM | LN DWMN: Limit Minimum Active Power operational function
Limit Watt | Watt Setting | DWMN.LimW or ReqWMin, WMinSptPct, WMinSpt | Requested minimum limiting setpoint of active power generation (or consumption)
Limit Watt | Enable | DWMN.ModEna
Limit Watt | Watt Setting | DWMX.LimW or ReqWMax, WMaxSptPct, WMaxSpt | Requested limiting setpoint of active power generation (or consumption)
Limit Watt | Enable | DWMX.ModEna
Nameplate | Supported Control Mode Functions | DWVR | LN DWVR: Active Power–Reactive Power (W-Var) operational function
Watt-VAR | Enable | DWVR.ModEna
Watt-VAR | P/Q Curve Points | DWVR.WVArCrv | Paired array of independent and dependent variables For crvPts: xVal = Percent of WMax (with increasing abscissas first optionally followed by decreasing abscissas for hysteresis ) yVal = Percent of VArMax or VArAvl Hysteresis path shall be described by adding points with decreasing abscissas at the end of the list of the points describing the initial path
Nameplate | Model | LPHD.PhyNam.model
Nameplate | Serial Number | LPHD.PhyNam.serNum
Nameplate | Version | LPHD.PhyNam.swRev
Nameplate | Manufacturer | LPHD.PhyNam.vendor
Frequency Trip | HF Trip Curve Points | PTOF.StrVal | Shall ride through value
Voltage Trip | HV Trip Curve Points | PTOV.TmVCrv new OpDITmms | (HysteresisSnapshotLN) Deactivation Delay. Intentional delay in ms before function deactivation, used to ensure that the frequency (voltage) is continuously stable during that time period within the normal frequency band between high HzStr (VStr) and low HzStr (VStr).
Momentary Cessation | HV Trip Curve Points | PTOV.TmVCrv new OpDITmms | (HysteresisSnapshotLN) Deactivation Delay. Intentional delay in ms before function deactivation, used to ensure that the frequency (voltage) is continuously stable during that time period within the normal frequency band between high HzStr (VStr) and low HzStr (VStr).
Frequency Trip | LF Trip Curve Points | PTUF.StrVal
Voltage Trip | LV Trip Curve Points | PTUV.TmVCrv new OpDITmms | (HysteresisSnapshotLN) Deactivation Delay. Intentional delay in ms before function deactivation, used to ensure that the frequency (voltage) is continuously stable during that time period within the normal frequency band between high HzStr (VStr) and low HzStr (VStr).
Momentary Cessation | LV Trip Curve Points | PTUV.TmVCrv new OpDITmms | (HysteresisSnapshotLN) Deactivation Delay. Intentional delay in ms before function deactivation, used to ensure that the frequency (voltage) is continuously stable during that time period within the normal frequency band between high HzStr (VStr) and low HzStr (VStr).